## Summary
SUMMARY SHEET FOR LEAKAGE BENCHMARKING IN SOUTH AFRICA | [9 empty] | Reference No.
S1. SYSTEM NAME AND CONTACT DETAILS
Name of Water Undertaking |  |  | 0
Name of Water Supply System |  |  | 0
Contact Details: |  |  | Name | 0
|  |  | Address | 0
0
0
|  |  | Telephone | 0
|  |  | Fax | 0
|  |  | E-mail | 0
S2. Performance Indicators of Water Loss
Viewpoint | Level | Parameter |  |  | Typical Range
[5 empty] | Excellent | Good | Poor | Actual PI | Units
Operations |  | % of year system is pressurised |  |  | 100 | 100 | <100 | 100 | %
management
of distribution | Basic
system at |  | Current Annual Real Losses (CARL) |  |  | 30 to 100 | 100 to 200 | >200 | 100.4566 | Litres/connection/day
current |  | (when system is pressurised - see note 2)
pressure
|  | Unavoidable Annual Real Losses (UARL) |  |  | n/a | n/a | n/a | 56.25 | Litres/connection/day
(see note 3)
| Detailed | Consumption |  |  | n/a | n/a | n/a | 1609.589 | Litres/connection/day
|  | Infrastructure Leakage Index (ILI) |  |  | 1 | 2 | >3.0 | 1.7859 | non dimensional
( = CARL/UARL : see note 4)
Financial |  | Volume of non-revenue water as a% of |  |  | <10% | 20% | 30% | 7.7895 | %
management | Basic | system input volume (see note 5)
aspects of
water losses | Detailed | Value of non-revenue water as a % of annual |  |  | <5% | 10% | 15% | 5.2933 | %
cost of running the system (see note 6)
Notes:
Note1: taken from data in "AQUA" article, December 1999 or estimated by WRP
Note 2: takes account of % of time system is pressurised, but not system pressure, density of connections or customet meter location
Note 3: takes account of density of connections and customer meter location at current pressure
Note 4: measures overall efficiency of management of distribution system at current operating pressure
Note 5: strongly influenced by average consumption per service connection
Note 6: Allows different values of Rand/m3 for different components of non-revenue water
S3. Key Operating Parameters which influence Unavoidable Annual Real Losses (UARL)
Variable | Typical Range
| Low | Medium | High | Actual PI | Units
Average Operating | 30 | 45 | 100 | 45 | Metres
Pressure
Density of | 20 | 45 | 120 | 40 | per km of mains
connections
4. Key Components of Annual System Input Volume
Component |  | m3/year |  | m3/connection/day | % of System
Input Volume
Water Exported |  | 1500 |  | not applicable | 0.0039474
Authorised Consumption |  | 33750000 |  | 1.5411 | 88.8158
excluding exports
Apparent Losses |  | 550000 |  | 0.025114 | 1.4474
Actual Consumption |  | 34300000 |  | 1.5662 | 90.2632
excluding exports
Real Losses |  | 2200000 |  | 0.10046 | 5.7895
|  |  |  | (see note 7) | (see note 8)
System Input Volume |  | 38000000 |  | 1.7352 | 100
Please return the completed form to R Mckenzie or J Kock at WRP Pretoria, tel: (012) 346 3496
Fax: (012) 346 9956
e-mail: wrp@wrp.co.za

## Detail-1
DATA ENTRY SHEET FOR LEAKAGE BENCHMARKING IN SOUTH AFRICA
Note: | Note: An example has been included to assist you in completing this data sheet. The example input data can be seen in the pale blue shaded areas. Your input data should appear in the pale yellow shaded areas. The light green shaded areas are protected calculation fields and nothing can be entered in these fields.
Use the units as shown. If you have to use other units; you have to change the appropriate cells.
D1. GENERAL
Name of Water Undertaking
Name of Water Supply System
| Contact Details: |  |  | Name
Address
Telephone
Fax
E-mail
D2. SYSTEM DATA
| Input Description |  |  |  |  | Variable | Example Data | Actual Data | Units
| Length of Mains (Transmission + Distribution) |  |  |  |  | Lm | 1500 | 1500 | km
| Number of Service Connections |  |  |  |  | Ns | 60000 | 60000 | Number | See Notes 1 & 2
| Density of Service Connections (per km of mains) |  |  |  |  | Ns/Lm | 40 | 40 | Per km
| Percentage of time system is pressurised during year |  |  |  |  | T | 100 | 100 | % | See Note 3
| Average operating pressure when system pressurised |  |  |  |  | P | 45 | 45 | metres | See Note 4
| Population served by the supply system |  |  |  |  | Pop | 100000 | 250000 | Number
Note 1: | The number of service connections is not always the same as the number of meters or billed accounts. For South African conditions, however, you can use the total of the number of metered accounts plus the estimated number of unmetered connections
Note 2: | In South Africa customer meters are usually located close to the street/stand boundary. If this is not the case for your system, then add a note here. |  |  |  | Insert your comments in this space.
Note 3: | Use T in % eg. If T = 80%, use 80 and not 0.8
Note 4: | If you do not have an accurate figure, please make a best estimate and provide brief details of how you derived it. |  |  |  | Insert your comments in this space.
D3. UNAVOIDABLE ANNUAL REAL LOSSES (UARL)
| Details |  |  |  | Calculation |  |  | Example Result | Actual Data | Units
| On mains |  |  |  | 18 x Lm x P x 365 x T/108 |  |  | 443.475 | 443.475 | 103 m3/yr
| On Service Connections |  |  |  | 0.8 x Ns x P x 365 x T/108 |  |  | 788.4 | 788.4 | 103 m3/yr
| Total Volume of UARL | [6 empty] | 1231.875 | 1231.875 | 103 m3/yr
| UARL in litres/service conn./day when the system is pressurised |  |  |  | Annual Volume of UARL x 106 / (Ns x 365 x T/100) |  |  | 56.25 | 56.25 | Litres/ conn./day
D4. ANNUAL WATER BALANCE DATA
D4a. Data Period
| 12-MONTH PERIOD FOR WHICH DATA APPLIES |  |  | Example Data |  | Actual Data
|  |  | Start Date | 1998-04-01
|  |  | End Date | 1999-03-31
D4b. System Input Volume
| Water Supplied | Example Data |  |  |  |  | Actual Data
|  | Metered 103 m3/yr | Correction to Source Meter data |  | Unmetered 103 m3/yr | Total 103 m3/yr | Metered 103 m3/yr | Correction to Source Meter data |  | Unmetered 103 m3/yr | Total 103 m3/yr
|  |  | +/- % | 103 m3/yr |  |  |  | +/- % | 103 m3/yr
| From Own Sources: | 36000 | 2% | 720 | 0 | 36720 | 36000 | 2% | 720 |  | 36720
| From Other Suppliers: | 1000 |  | 0 | 280 | 1280 | 1000 |  | 0 | 280 | 1280
| Total: | 37000 |  | 720 | 280 | 38000 | 37000 |  | 720 | 280 | 38000
D4c. Components of Authorised Consumption
| Components of Authorised Consumption | Example Data |  |  |  |  | Actual Data
|  | Billed Metered 103 m3/yr | Billed Unmetered 103 m3/yr | Unbilled Metered 103 m3/yr | Unbilled Unmetered 103 m3/yr | Total 103 m3/yr | Billed Metered 103 m3/yr | Billed Unmetered 103 m3/yr | Unbilled Metered 103 m3/yr | Unbilled Unmetered 103 m3/yr | Total 103 m3/yr
| Water Exported: | 1500 | 0 | 0 | 0 | 1500 | 1500 |  |  |  | 1500
| Households: | 24500 | 500 | 0 | 0 | 25000 | 24500 | 500 |  |  | 25000
| Non-households: | 6900 | 100 | 0 | 0 | 7000 | 6900 | 100 |  |  | 7000
| Standpipes: | 0 | 500 | 10 | 0 | 510 |  | 500 | 10 |  | 510
| Firefighting: | 0 | 0 | 0 | 100 | 100 |  |  |  | 100 | 100
| Mains Flushing: | 0 | 0 | 0 | 100 | 100 |  |  |  | 100 | 100
| Building water: | 1040 | 0 | 0 | 0 | 1040 | 1040 |  |  |  | 1040
| Other (specify): |  |  |  |  | 0 |  |  |  |  | 0
| Other (specify): |  |  |  |  | 0 |  |  |  |  | 0
| TOTALS: | 33940 | 1100 | 10 | 200 | 35250 | 33940 | 1100 | 10 | 200 | 35250
D4d. Components of Water Losses
| Details |  |  |  |  | Example Result | Actual Result | Units
| Water Losses = System Input – Authorised Consumption |  |  |  |  | 2750 | 2750 | 103 m3/yr
| Percentage of Total Losses estimated to represent the Apparent Losses |  |  |  |  | 20 | 20 | %
| Apparent Losses |  |  |  |  | 550 | 550 | 103 m3/yr
| Annual Real Losses (ARL) = Water Losses – Apparent Losses |  |  |  |  | 2200 | 2200 | 103 m3/yr
D5. SELECTED OPERATIONAL PERFORMANCE INDICATORS
D5a. Current Annual Real Losses per Connection (CARL) at Current Pressures
| Details |  |  |  | Calculation |  |  | Example Result | Actual Result | Units
| CARL is expressed in Litres/service connection/day, when system is pressurised |  |  |  | ARL x 106 / (Ns x T/100 x 365) |  |  | 100.4566 | 100.4566 | Litres /conn./day
| Consumption in litres/conn/day | [6 empty] | 1609.589 | 1609.589 | Litres /conn./day
D5b. Infrastructure Leakage Index (ILI)
| Details |  |  |  | Calculation |  |  | Example Result | Actual Result
| ILI is the ratio of Current Annual Real Losses (CARL) to Unavoidable Annual Real Losses |  |  |  | CARL / UARL |  |  | 1.7859 | 1.7859
D5c. Non-Revenue Water as a % by Volume of System Input
| Description of Unbilled Items |  | Example Result |  |  | Actual Result
|  |  | Volume | System Input | % of System Input | Volume | System Input | % of System Input
|  |  | 103 m3/yr | 103 m3/yr |  | 103 m3/yr | 103 m3/yr
| Unbilled Consumption |  | 210 | 38000 | 0.55263 | 210 | 38000 | 0.55263
| Apparent Losses: |  | 550 | 38000 | 1.4474 | 550 | 38000 | 1.4474
| Real Losses: |  | 2200 | 38000 | 5.7895 | 2200 | 38000 | 5.7895
| Total Unbilled: |  | 2960 | 38000 | 7.7895 | 2960 | 38000 | 7.7895
D6. SELECTED FINANCIAL PERFORMANCE INDICATORS
D6a. Local Valuation of Real and Apparent Losses
| Details |  |  |  | Example Result | Actual Result |  | Units
| Unit Value of Real Losses (eg bulk purchase price) |  |  |  | 0.15 | 0.15 |  | R /m3
| Unit Value of Apparent Losses (eg selling price) |  |  |  | 2.7 | 2.7 |  | R /m3
D6b. Annual Cost of Running System
| Details |  |  | Example Cost |  | Actual Cost |  | Units
| Annual Cost of running system in 1000's of Rand per year |  |  | 45000 |  | 45000 |  | 103 R/year
D6c. Non-Revenue Water as % by Value of Cost of Running System
| Description of Unbilled Items |  | Example Result |  |  |  | Actual Result
|  |  | Volume | Unit Value | Value | % of Annual Running Costs | Volume | Unit Value | Value | % of Annual Running Costs
|  |  | 103 m3/yr | R /m3 | 103 R/year | Costs | 103 m3/yr | ( R /m3 ) | 103 R/year | Costs
| Unbilled Consumption |  | 210 | 2.7 | 567 | 1.26 | 210 | 2.7 | 567 | 1.26
| Apparent Losses: |  | 550 | 2.7 | 1485 | 3.3 | 550 | 2.7 | 1485 | 3.3
| Real Losses: |  | 2200 | 0.15 | 330 | 0.73333 | 2200 | 0.15 | 330 | 0.73333
| Total Unbilled: |  | 2960 |  | 2382 | 5.2933 | 2960 |  | 2382 | 5.2933

## Detail-2
D7. RELATIONSHIP BETWEEN REAL LOSSES EXPRESSED AS % OF SYSTEM INPUT
D7a. Real losses curve definition
Curve Definition
Consumption |  | Real losses in litres/service connection/day
litres/serv conn/day |  | 50 | 100 | 200 | 500 | 1000
100 |  | 33.3333 | 50 | 66.6667 | 83.3333 | 90.9091
250 |  | 16.6667 | 28.5714 | 44.4444 | 66.6667 | 80
500 |  | 9.0909 | 16.6667 | 28.5714 | 50 | 66.6667
1000 |  | 4.7619 | 9.0909 | 16.6667 | 33.3333 | 50
2000 |  | 2.439 | 4.7619 | 9.0909 | 20 | 33.3333
3000 |  | 1.6393 | 3.2258 | 6.25 | 14.2857 | 25
5000 |  | 0.9901 | 1.9608 | 3.8462 | 9.0909 | 16.6667
10000 |  | 0.49751 | 0.9901 | 1.9608 | 4.7619 | 9.0909
D7b. Components of water balance in litres/service connection/day (Actual Results)
Billed
|  |  | Authorised |  |  |  | Revenue
|  |  | Consumption |  |  |  | Water
|  |  | = |  | Authorised
|  |  | 1600 |  | Consumption |  | 1600
| Total |  | Unbilled |  | =
System | Consumption |  | Authorised |  | 1609.589
Input | = |  | Consumption
Volume | 1634.7032 |  | =
= |  |  | 9.589 |  |  |  | Non-Revenue
1735.1598 |  |  | Apparent |  |  |  | Water
|  |  | Losses |  |  |  | =
|  |  | = |  | Total |  | 135.1598
|  |  | 25.1142 |  | Losses
| Real |  |  |  | =
| Losses |  |  |  | 125.5708
=
100.4566
D7c. Current Real Losses as % of System Input Volume
Details |  | Calculation |  |  |  | Actual Result | Units
System Input Volume |  | from D7b |  |  |  | 1735.1598 | Litres/conn/day
Total Consumption |  | from D7b |  |  |  | 1634.7032 | Litres/conn/day
Annual Real Losses |  | from D7b |  |  |  | 100.4566 | Litres/conn/day
ARL as % of System Input |  | ARL / System input volume x 100 |  |  |  | 5.7895 | %
D7d. Potential Real Losses as % of System Input Volume
Details |  |  | Calculation |  |  |  |  | Actual Result | Units
Unavoidable Annual Real Losses (UARL) |  |  | from D3 |  |  |  |  | 56.25 | Litres/conn/day
Target Loss Factor (TLF) |  |  | User defined for each system |  |  |  |  | 2 | Dimensionless
Target Annual Real Losses (TARL) |  |  | TLF x UARL |  |  |  |  | 112.5 | Litres/conn/day
Current Annual Real Losses (CARL) |  |  | CARL from D5a |  |  |  |  | 100.4566 | Litres/conn/day
Potential savings |  |  | CARL - TARL |  |  |  |  | -12.0434 | Litres/conn/day
Potential ARL as % of System Input |  |  | TARL / (System input volume-Potential savings) x 100 |  |  |  |  | 6.4389 | %
D7e. Real Losses as a % of System Input Volume versus Consumption in litres/service connection/day,
for different values of Real Losses in litres/service connection/day